This Scope of Work (SOW) provides a concise, technical breakdown for the Blacktech Solutions Corp electrical build-out. It covers the full 30-day timeline across four distinct phases, totaling approximately 850 words to ensure clarity and professional brevity.

PROJECT OVERVIEW: WAREHOUSE & OFFICE BUILD-OUT

Contractor: Blacktech Solutions Corp (Derrell Black)

Location: 14076 Lincoln Ave

Timeline: 30 Days (4 Phases)

Objective: Upgrade legacy T12 lighting to high-efficiency LED, install 8 industrial heaters, 1 RTU service, and complete all office power/lighting requirements.

### PHASE 1: SITE INFRASTRUCTURE & OVERHEAD DOORS (WEEK 1)

Phase 1 focuses on safety, accessibility, and temporary power to support concurrent trades (Plumbing/HVAC).

* Temporary Lighting & Power:

* Installation of high-lumen LED "spider" stringers throughout the warehouse.

* Mounting height: Minimum 8' AFF to clear equipment.

* Placement of a temporary 120V GFCI-protected distribution hub for construction tools.

* Overhead Door Electrical:

* Installation of three (3) dedicated 20A, 120V circuits using EMT conduit.

* Rough-in and termination of 3-button control stations (Open/Close/Stop) at each door.

* Wiring of low-voltage safety photo-eye sensors at the base of the tracks.

* Final "whip" connections to the motor operators using 1/2" Liquid-tight flexible conduit.

### PHASE 2: WAREHOUSE LIGHTING RETROFIT (WEEK 2)

Phase 2 targets energy efficiency and the acquisition of the $5,865 utility rebate by removing legacy T12 technology.

* F2 Retrofit (51 Units):

* Demolition: Complete removal of 102 T12 lamps and 51 magnetic ballasts from existing 12ft tandem housings.

* Installation: Integration of UL Type B LED Retrofit Kits (8ft + 4ft strip inserts).

* Wiring: Direct-wire conversion (Ballast Bypass) to 120-277V line voltage.

* Compliance: All components must be DLC 5.1 Premium listed.

* Hazardous Waste Management:

* Palletizing of mercury-containing T12 tubes.

* Transport to a certified recycling facility with documented Receipt of Disposal for rebate verification.

### PHASE 3: INDUSTRIAL HEATING & HVAC SERVICE (WEEK 3)

Phase 3 manages high-load mechanical electrical requirements.

* Ceiling Heaters (8 Units):

* Structural: Mechanical anchoring of 8 industrial heaters to steel bar joists using 3/8" all-thread rod and 1-5/8" Unistrut.

* Circuitry: Installation of 8 dedicated 240V, 30A circuits using #10 AWG THHN copper wire.

* Controls: Installation of 8 wall-mounted, line-voltage thermostats positioned for optimal thermal sensing.

* RTU Electrical Service:

* Run one dedicated 240V/3-Phase (or 1-Phase) circuit from the main panel to the rooftop.

* Installation of a NEMA 3R Weatherproof Disconnect within 10ft of the RTU.

* Installation of a 120V GFCI service outlet on the roof (NEC 210.63 compliance).

### PHASE 4: OFFICE FINISH & PANEL INTEGRATION (WEEK 4)

The final phase covers the office "trim-out" and the critical balancing of the main electrical service.

* Office Devices & Lighting:

* F1 Lighting: Installation of 34 recessed 2x2 LED panels in the grid ceiling.

* Receptacles: Installation of 45 commercial-grade 20A duplex outlets and 8 GFCI outlets (Breakroom/Restrooms).

* Switching: Installation of 12 toggle switches and 4 occupancy sensors to meet energy codes.

* Conference Room: Installation of one brass pop-up floor box for AV/Power.

* Main Panel Balancing:

* Space Management: Consolidation of existing 120V circuits using tandem/twin breakers to accommodate the 18 new 240V heater/RTU poles.

* Load Test: Simultaneous staggered start-up of all 8 heaters to verify the main 200A/400A breaker remains within safe operating temperatures.

* Labeling: Application of a new, typed circuit directory for the entire facility.

### TECHNICAL REQUIREMENTS & STANDARDS

* Code Compliance: All work performed by Blacktech Solutions Corp shall adhere to the 2026 National Electrical Code (NEC) and local Chicago/Illinois amendments.

* Materials: All branch wiring to be 12/2 MC Cable (Office) or EMT Conduit (Warehouse). Only Spec-Grade 20A devices are authorized for installation.

* Rebate Administration: Blacktech will provide all technical specs, disposal receipts, and signed inspection reports required by the utility company to facilitate the $5,865 incentive check.

### PROJECT TOTALS

* Gross Contract Value: $51,460.00

* Estimated Utility Rebate: ($5,865.00)

* Net Project Cost: $45,595.00

Next Step: I can generate the official Material Procurement List for Week 1 so your crew has the overhead door controls and temp lights ready for Monday morning. Would you like me to do that?